## Sheet6
Operation Number	Attachment Action: / ( I )nstalling / ( R )emoving / ( E )xisting	Pole Owner	Pole #	Pole Structure	Proposed Riser (Yes/No) &	Proposed Guy (Yes/No) &	PLA (%) with proposed attachment	Construction Grade of Analysis	Existing Mid-Span Data		Make Ready Data
												Attachment Height		Mid-Span / (same span as existing)
									Height Lowest Com	Height Lowest CPS Electrical	Attacher Description	Existing	Proposed	Proposed
1	( I )nstalling	CPS	PL410620	40-4 Southern Pine	NO	NO	78.70%	C	14'-10"	23'10"	Neutral	29'-6"
											CPS Supply Fiber	28'-0"
											Charter/Spectrum Fiber Optic		24'-7"	21'-1"
											AT&T Fiber Optic Com	23'-7"
											AT&T Telco Com	22'-4"
											AT&T Com Drop	21'-5"		15'-10"
									From Pole	To Pole
									PL410620	PL398491
2	( I )nstalling	CPS	PL398491	45-2 Southern Pine	YES (1)	YES (1)	62.08%	C	NA	NA	Neutral	27'-1"
											CPS Top Bracket Street Light	26'-3"	24'-7"
											CPS Supply Fiber	25'-8"
											CPS Bottom Bracket Street Light	25'-7"	23'-11"
											CPS Supply Fiber	25'-6"
											CPS Secondary Drip Loop	25'-5"	26'-7"
											CPS Street Light Drip Loop	24'-9"	23'-4"
											Charter/Spectrum Fiber Optic		22'-4"	UG
											Charter/Spectrum Down Guy		22'-4"
											AT&T Fiber Optic Com	21'-4"		16'-4"
											AT&T Telco Com	20'-4"		15'-1"
											AT&T Com Drop	19'-8"
											AT&T Com Drop	19'-8"
											AT&T Com Drop	19'-6"
											AT&T Com Drop	19'-5"
											CPS Energy Down guy	33'-9"
											CPS Energy Down guy	26'-4"
											Charter Communication Riser		21'-4"
											Ref (North East) to service pole
											CPS Service	27'-1"		18'-0"
											AT&T Com Drop	19'-8"		11'-10"
											AT&T Com Drop	19'-6"		11'-9"
											Ref (South East) to Pl401451
											Neutral	26'-11"

									From Pole	To Pole
									PL398491	PL401451
3	( I )nstalling	CPS	PL389359	45-4 Southern Pine	YES (1)	YES (1)	84.86%	C	17'-8"	22'-8"	Neutral	27'-3"
											CPS Supply Fiber	25'-9"
											Charter/Spectrum Fiber Optic		23'-0"	18'-8"
											Charter/Spectrum Down Guy		23'-0"
											AT&T Fiber Optic Com	22'-8"	22'-0"	17'-3"
											AT&T Telco Com	21'-8"	21'-0"	16'-3"
											Backspan
											Charter Communication Riser	22'-0"
											Ref (North East) PL413713
											Neutral	27'-3"
											Ref (North West) to PL1401451
											Neutral	27'-3"
											CPS Supply Fiber	25'-9"
									From Pole	To Pole	AT&T Fiber Optic Com	22'-8"	22'-0"	20'-1"
									PL389359	PL404474	AT&T Telco Com	21'-8"	21'-0"	17'-10"
4	( I )nstalling	CPS	PL404474	40-3 Southern Pine	NO	NO	59.84%	C	19'-6"	23'-8"	Neutral	26'-0"
											CPS Street Light Feed	26'-0"		24'-6"
											CPS Supply Fiber	24'-6"
											CPS Top Bracket Street Light	23'-6"
											CPS Drip Loop Street Light	23'-0"
											Charter/Spectrum Fiber Optic		21'-7"	21'-3"
											AT&T Fiber Optic Com	22'-9"	20'-7"	19'-1"
											AT&T Telco Com	21'-7"	19'-7"	18'-0"
									From Pole	To Pole
									PL404474	PL900997
5	( I )nstalling	CPS	PL900997	45-2 Southern Pine	YES (1)	YES (1)	64.73%	C	NA	NA	Neutral	27'-1"
											CPS Street Light Feed	27'-1"
											CPS Supply Fiber	25'-10"
											CPS Drip Loop Secondary	25'-8"
											CPS Top Bracket Street Light	25'-0"
											CPS Drip Loop Street Light	23'-11"
											Charter/Spectrum Fiber Optic		21'-6"	UG
											Charter/Spectrum Down Guy		21'-6"
											AT&T Fiber Optic Com	21'-6"	20'-6"
											AT&T Telco Com	20'-6"	19'-6"
											Charter Communication Riser		20'-6"
											Ref (South East) to service pole
											CPS Service	27'-1"		18'0"
											Ref (South East) to PL398490
											Neutral	27'-1"
											CPS Supply Fiber	25'-10"
											AT&T Fiber Optic Com	21'-6"	20'-6"	21'-7"
											AT&T Telco Com	20'-6"	19'-6"	20'-6"
									From Pole	To Pole
									PL900997	PL398490
6	( I )nstalling	CPS	PL370858	45-2 Southern Pine	YES (1)	YES (1)	42.55%	C	20'-8"	21'-7"	Neutral	26'-6"
											CPS Supply Fiber	25'-5"
											Charter/Spectrum Fiber Optic		22'-1"	22'-1"
											AT&T Fiber Optic Com	22'-10"	21'-1"	20'-9"
											AT&T Telco Com	21'-10"	20'-1"	19'-10"
											Charter Down Guy		22'-1"
											Backspan
											Charter Communication Riser		21'-1"
											Ref (North West) to PL379971
											Neutral	26'-6"
											CPS Supply Fiber	25'-5"
									From Pole	To Pole	AT&T Fiber Optic Com	22'-10"	21'-10"	17'-5"
									PL370858	PL3268481	AT&T Telco Com	21'-10"	20'-10"	17'-0"